## Table 1
OSU Requirements for Sustainable Development: New Construction and Major Renovation
Project: Withycombe Renovation 2022 | [5 empty] | Prerequisite
Easiest to achieve for most projects/sites
May be easy to achieve for some projects
Project dependent, highly specific, more effort
Purple denotes Regional Priority | [5 empty] | Not Available
|  |  | Campus Office/Classroom Buildings |  |  |  |  | Other Programs
|  |  | Y | ? | N
1 | IP | Integrative Process | 1 |  |  | Prior to Design Development, conduct preliminary analysis of energy and water systems options; convene goals setting workshop. |  | ETO $
15 |  | Location and Transportation | 12 | 0 | 3 | Campus Office/Classroom Buildings |  | Other Prog.
15 | LT | LEED for ND Location
1 | LT | Sensitive Land Protection | 1 |  |  | Most OSU property has been previously developed. Previously developed: altered by paving, construction, and/or land use that would typically have required regulatory permitting to have been initiated. This includes landscaping. Land that is not previously developed and landscapes altered by current or historical clearing or filling, agricultural or forestry use, or preserved natural areas are considered undeveloped land. |  | STARS OP 10
2 | LT | High Priority Site |  |  | 2 | Most of the campus is within the Historic District; surrounding building density may comply with infill requirements in many cases. 2 pt option requires Brownfield Redevelopment.
5 | LT | Surrounding Density and Diverse Uses | 5 |  |  | Per OSU all points will have compliance Density: 22,000 sf/acre = 2 pts or 35,000 sf/acre = 3 pts Diverse Uses: 4-7 services= 1 pt; 8+ = 2 pts
5 | LT | Access to Quality Transit | 5 |  |  | Corvallis Transit System (CTS) serves multiple stops with multiple lines through campus. Two lines run both directions at stops close to many project sites. CTS offers no Sunday service on any line but weekend daily trip average should comply. |  | STARS OP 18
1 | LT | Bicycle Facilities | 1 |  |  | Short term bike storage spaces for 2.5% of peak visitors (min 4) within ~100 ft of main entrance AND; covered bike storage spaces for 30% of regular occupants (min 1 space per unit) within ~100 ft of any functional entrance AND; storage is within ~200 yd of compliant bike network. |  | STARS OP 18
0 | LT | Reduced Parking Footprint |  |  |  | Projects with parking and earning points for Diverse Uses above must reduce capacity 40% below baseline according to use type, AND reserve minimum 5% of spaces for carpool only.
1 | LT | Green Vehicles |  |  | 1 | Designate min 5% of all parking spaces used by the project building as preferred parking for green vehicles (ACEEE 45 or better); OR discount parking rate at least 20% for those vehicles; AND either install EVSE in 2% of remaining spaces OR install other alternative fuel fueling facilities. |  | STARS OP 18
10 |  | Sustainable Sites | 2 | 0 | 8 | Campus Office/Classroom Buildings
REQ | Prereq | Construction Activity Pollution Prevention | Y |  |  | Control soil erosion, waterway sedimentation, airborne dust implementing an ESC Plan per EPA CGP
1 | SS | Site Assessment |  |  | 1 | Conduct Site Inventory and Analysis of multiple features and impact of the site features on project design |  | STARS OP 10
2 | SS | Site Development - Protect or Restore Habitat | 2 |  |  | IF determined to be previously developed, THEN 2 points for restoration of at least 30% of project site; including and restoring all soil in revegetated areas.
1 | SS | Open Space |  |  | 1 | 30% of total site area to be pedestrian oriented open space; of that 30%, 25% must be vegetated (or have overhead vegetated cover). Turf grass does not count as vegetated.
3 | SS | Rainwater Management (@3pts) |  |  | 3 | Managed site runoff from a 95th percentile storm event onsite using LID/green infrastructure; Manage 98th percentile event for 3rd point.
2 | SS | Heat Island Reduction |  |  | 2 | 75% of roof areas compliant (high SRI or vegetated) plus 50% nonroof hardscape compliant (SR)
1 | SS | Light Pollution Reduction |  |  | 1 | Requires early site lighting plan with trespass compliance at project boundaries, glare, and uplight limits. Requires photometric plan plus calculations. NO Due to OSU standard Visco light poles exceeding B.U.G. limits at site boundary Roadway Classification Type V Longitudinal Classification Short Upward Waste Light Ratio 0.04 Luminaire Efficacy Rating (LER) 127 Maximum UGR 38.7 BUG Rating B3-U3-G2
9 |  | Water Efficiency | 3 | 0 | 6 | Campus Office/Classroom Buildings
REQ | Prereq | Outdoor Water Use Reduction | Y |  |  | Reduce by 30% from baseline for peak month. Reductions must be achieved through plant species selection and irrigation system efficiency. Consider initiating a native and adapted planting program with new projects.
REQ | Prereq | Indoor Water Use Reduction | Y |  |  | Aggregate indoor use 20% below EPAct 2005 baseline. New eligible fixtures WaterSense labeled. |  | STARS OP 22
REQ | Prereq | Building-Level Water Metering | Y |  |  | Monthly data required. OSU standard metering meets this requirement.
2 | WE | Outdoor Water Use Reduction | 1 |  | 1 | Reduce by 50% from baseline for peak month using plant selection and irrigation efficiency for 1 pt. Reductions beyond 30% may use any combination of efficiency, alternative water sources, and smart scheduling technologies. |  | STARS OP 23
6 | WE | Indoor Water Use Reduction (req 4pts) | 2 |  | 4 | Plan 30% reduction from EPAct 2005; savings of 40% adds 2 points plus 1 Regional Priority point |  | STARS OP 22
0 | WE | Cooling Tower Water Use |  |  |  | Maximize number of cycles (up to 10) without exceeding filtration levels or affecting operation of condenser water system. Applicable only on projects with Cooling Towers. Second point not reasonable goal.
1 | WE | Water Metering |  |  | 1 | Irrigation already metered. Must meter one other subsystem. Recommend hot water or process water.
33 |  | Energy and Atmosphere | 18 | 0 | 15 | Campus Office/Classroom Buildings
REQ | Prereq | Fundamental Commissioning and Verification | Y |  |  | Standard Cx, following ASHRAE Guideline 0-2005 & ASHRAE Guideline 1.1–2007 for HVAC&R Systems |  | ETO $
REQ | Prereq | Minimum Energy Performance | Y |  |  | Perform whole building energy modeling. Demonstrate minimum of 5% energy cost savings from baseline (ASHRAE 90.1-2010) case
REQ | Prereq | Building-Level Energy Metering | Y |  |  | Building level metering. OSU standard metering meets this requirement.
REQ | Prereq | Fundamental Refrigerant Management | Y |  |  | No new chlorofluorocarbon (CFC)-based refrigerants
6 | EA | Enhanced Commissioning | 3 |  | 3 | Enhanced CxA must be engaged by mid DD phase and start OPR-BOD-design reviews; post- occ site visit; Systems Manual. Consider adding verification monitoring to all projects for the 4th point. This benefits the university managing energy use. Consider the Building Envelope Cx to assure physical connections are as intended and to identify infiltration and energy loss/gain for long term operability. |  | ETO $
18 | EA | Optimize Energy Performance | 14 |  | 4 | Option 1: Using analysis for EA P2: Minimum Energy Performance, demonstrate a percentage improvement in the design building performance as energy cost savings. Points awarded from 1 pt for 6% to 18 pts for 50%. Option 2: follow ASHRAE Advanced Energy Design Guide. |  | ETO $ STARS OP 5
1 | EA | Advanced Energy Metering | 1 |  |  | Main building meter plus meter any individual energy end uses that represent ~10% or more of annual total. Work with Sustainability Office to develop alternatives to 10% if needed.
2 | EA | Demand Response (@1pt) |  |  | 2 | Develop plan for shedding at least 10% of building estimated peak demand. Include DR in Cx review. NO utility option for Corvallis power
3 | EA | Renewable Energy Production (@2.5%) |  |  | 3 | 1% = 1 pt; 5% = 2 pts; 10% = 3 pts. Aggregated solar is acceptable. Possible to pool funding to develop on solar friendly sites. |  | ETO $
1 | EA | Enhanced Refrigerant Management |  |  | 1 | Use only refrigerants with ozone depletion potential (ODP) of zero and a global warming potential (GWP) of less than 50.
2 | EA | Green Power and Carbon Offsets |  |  | 2 | Contract for Green Power/RECs and or Carbon Offsets for 50% or 100% of total energy use annually for five years. REC's apply only to Electricity scope; Carbon offsets apply to all energy types used. |  | STARS OP 1 STARS OP 6
13 |  | Materials and Resources | 8 | 0 | 5 | Campus Office/Classroom Buildings
REQ | Prereq | Storage and Collection of Recyclables | Y |  |  | Provided dedicated waste centers for hauling and storage for entire building. |  | STARS OP 19
REQ | Prereq | Construction & Demo Waste Management Planning | Y |  |  | Identify at least 5 materials targeted for diversion, and plan where the material will be taken, and how the facility will process it. |  | STARS OP 20
5 | MR | Building Life-Cycle Impact Reduction | 5 |  |  | Attainable 5 points for reusing an historic building, or 2-3 points for reusing 25-50% as percentage of the surface area. OR Whole-Building LCA could be performed and reported for 3 pts
2 | MR | BPDO-EPD's (@1pt) | 1 |  | 1 | 20 products with Type III EPDs; 1/2 credit for generic EPDs; 1/4 credit for ISO 14044 conforming LCAs. OSU may create design library of conforming materials to make this simple to scale and repeat.
2 | MR | BPDO-Sourcing (@1pt) |  |  | 2 | 25% (by cost) of permanently installed products have documentation of compliant sourcing practices. Double count products sourced within 100 miles. Difficult to track the 100% costs of all divisions of project work.
2 | MR | BPDO Material Ingredients | 1 |  | 1 | 20 products have ingredient reporting documentation - HPD, compliant CASRN, C2C Bronze = 1 pt; Optimization additional point unlikely. OSU may create a design library of conforming materials to make this simple to scale and repeat.
2 | MR | Construction and Demolition Waste Management | 1 |  | 1 | Divert 50% waste/3 streams = 1 pt Divert 75% waste/4 streams = 1 pt - if demo in project not likely |  | STARS OP 20
16 |  | Indoor Environmental Quality | 8 | 0 | 8 | Campus Office/Classroom Buildings
REQ | Prereq | Minimum Indoor Air Quality Performance | Y |  |  | Requires minimum ASHRAE 62.1–2016 or Oregon Mechanical Code whichever is more stringent. Include airflow monitoring
REQ | Prereq | Environmental Tobacco Smoke Control | Y |  |  | Met by OSU policy.
2 | IEQ | Enhanced Indoor Air Quality Strategies | 1 |  | 1 | Entryway systems, contain and exhaust chemical mixing spaces, MERV 13 permanent filters for 1 pt Either exterior contamination prevention; OR increased ventilation (+30%); OR CO2 monitoring; OR additional source control for 1 pt
3 | IEQ | Low-Emitting Materials | 2 |  | 1 | Compliance thresholds for (2 products = 1pt; 4 = 2pt; 5 = 3pt) Paints+Coatings: 90% emissions/100% VOC limits Adhesives+Sealants: 90% emissions/100% VOC limits Flooring: 100% CDPH Standard Method v1.1-2010 for general emissions standards Composite wood: 100% CARB ATCM for ULEF materials Walls, Ceilings, Thermal & Acoustic Insulation: 100% CDPH Standard Method v1.1-2010 for general Emissions Furniture N/A
1 | IEQ | Construction IAQ Management Plan | 1 |  |  | During construction, meet or exceed all applicable recommended control measures of the Sheet Metal and Air Conditioning National Contractors Association IAQ Guidelines for Occupied Buildings under Construction, 2nd edition, 2007, ANSI/SMACNA 008–2008, Chapter 3.
2 | IEQ | Indoor Air Quality Assessment | 1 |  | 1 | Full replacement ventilation (flush-out) = 1 pt - schedule sensitive AQ testing = 2 pts: One time AQ testing more time efficient and could be more cost effective than flush-out, but must test until all spaces pass. Could test in-house.
1 | IEQ | Thermal Comfort | 1 |  |  | Design to ASHRAE Standard 55–2010 thermal comfort; provide active temperature control to 50% of individual occupant spaces. Design into non-res buildings.
2 | IEQ | Interior Lighting | 1 |  | 1 | 3 level controls req'd for 90% of individual occupant spaces plus added controls in all shared spaces = 1pt; Quality lighting requires low glare; CRI 80 min; long rated life; and less than 25% direct overhead lighting. Other options require surface reflectance and illuminance calcs.
3 | IEQ | Daylight | 1 |  | 2 | 55% or 75% of floor area required to demonstrate sDA with ASE limits. Include window coverings for glare control. 55% set as reasonable OSU target, with the right design using narrow building footprints and maximizing window locations and size options.
1 | IEQ | Quality View |  |  | 1 | Views to outdoors for 75% of regularly occupied floor area. Applicable options are: flora & sky; objects min 25' away; unobstructed view within 3 times head height of vision glazing. Design considerations as in Daylighting but this is a highly recommended element for education and office projects.
1 | IEQ | Acoustic Performance |  |  | 1 | HVAC Background noise <35/40 dBA in units; max STC of 55/50 to adjacent spaces; limit space reverb time to <0.6. This is a high priority for occupant satisfaction and productivity.
6 |  | Innovation | 3 | 0 | 0 | Campus Office/Classroom Buildings
1 | ID | Innovation: EQ Thermal Comfort Survey | 1 |  |  | IEQ Thermal Comfort required
1 | ID | Innovation: Education |  |  |  | Apply standard template (to be developed) for student and public education, tours, signage, webpage. This can be a student led and implemented project but with some cost to direct, review, and manage the requirements. |  | STARS EN 2 + EN 8
1 | ID | Innovation: Mold Prevention Plan | 1 |  |  | From Schools Standard; would extend material and building service life/protect occupants
1 | ID | Exemplary Performance: |  |  |  | To be determined by project.
Innovation: Rain water collection Cistern
1 | ID | LEED Accredited Professional | 1
4 |  | Regional Priority (EOGO) max 4 of 6 available | 1 | 0 | 0
0 | RP | SS Rainwater management @3 pts |  |  | 0
0 | RP | WE Indoor water use reduction @ 4pts |  |  | 0
1 | RP | EA Demand response @ 1pt |  |  | 0
1 | RP | EA Renewable energy production @ 2pts (5%) |  |  | 0 |  | Solar
1 | RP | MR BPDO-EPDs @1 pt | 1
1 | RP | MR BPDO-Sourcing @ 1pt |  |  | 0
107 TOTALS |  |  | 56 | 0 | 45
Acceptable: 50 to 59 points; Outstanding: 60 to 79 points, Exemplary: 80 to 110 | [6 empty] | Glossary
ACEEE - American Council for an Energy-Efficient Economy
AQ - Air Quality
ASE - Annual Sunlight Exposure
ATCM - Airborne Toxic Control Measures
BPDO - Building Product Disclosure & Optimization
C2C - Cradle to Cradle
CARB - California Air Resources Board
CASRN - CAS Registry Number
CDPH - California Department of Public Health
CRI - Color Rendering Index
Cx - Commissioning
CxA - Commissioning Authority
DD - Design Development
DR - Demand Response
EPA CGP - Environmental Protection Agency's Construction General Permit
EPAct - Energy Policy Act
EPD - Environmental Product Declaration
ESC - Erosion and Sediment Control
EVSE - Electric Vehicle Service Equipment
HC -
HPD - Health Product Declaration
IAQ - Indoor Air Quality
IEQ - Indoor Environmental Quality
LCA - Life Cycle Assessment
MERV - Minimum Efficiency Reporting Value
MR - Mercury Required
OPR-BOD - Owner Project Requirements-Basis of Design
PBT - Polybutylene Terephthalate
REC - Renewable Energy Certificate
sDA - Spatial Daylight Autonomy
SRI - Solar Reflectance Index
STC - Sound Transmission Class
ULEF - Ultra-low Emitting Formaldehyde